## Sheet1
Runner Pitch Dia. (in) | 3.4
Nozzle Diameter (in) | 0.669
Nozzle Discharge Coefficient (Cd) | 0.98
Net Head (ft) | 92
Entrance Angle | 20 | Pelton =0, Turgo=20 Typ.
Bucket Velocity Coefficient (Cb) | 0.96
Exit Angle | 10
Ideal Spouting Velocity (ft/sec) | 76.9727
Actual Spouting Velocity (ft/sec) | 75.4333
RPM at 50% Vjet ideal | 2594.2424
Single Nozzle Flow Rate (cfs) | 0.18414
Single Nozzle Flow Rate (gpm) | 82.641
Single Nozzle Mass Flow (lb/sec) | 11.4902
Theoretical Shaft Power (hp) | 1.922
Generator Efficiency | 82%
Electric Power (kW) | 1.1753
Number of nozzles | 2
Total Power (kW) | 2.3505
| Runner Speed |  | Tangential Component of
| Ideal Basis (B9) |  | Momentum (lbm-ft/sec^2)
| %Vjet | u (ft/sec) | In | Out | Force (lbf) | rpm | Torque (ft-lbf) | Power (hp) | Efficiency (%)
| 100 | 76.9727 | -16.6219 | 16.7231 | -1.0356 | 5188.4849 | -0.1467 | -0.14493 | -7.5404
| 98 | 75.4333 | 0 | 0 | 0 | 5084.7152 | 0 | 0 | 0
| 96 | 73.8938 | 16.6219 | -16.7231 | 1.0356 | 4980.9455 | 0.1467 | 0.13913 | 7.2388
| 94 | 72.3544 | 33.2437 | -33.4462 | 2.0711 | 4877.1758 | 0.29341 | 0.27246 | 14.176
| 92 | 70.8149 | 49.8656 | -50.1693 | 3.1067 | 4773.4061 | 0.44011 | 0.4 | 20.8116
| 90 | 69.2755 | 66.4875 | -66.8924 | 4.1422 | 4669.6364 | 0.58682 | 0.52174 | 27.1456
| 88 | 67.736 | 83.1093 | -83.6155 | 5.1778 | 4565.8667 | 0.73352 | 0.63768 | 33.1779
| 86 | 66.1965 | 99.7312 | -100.3386 | 6.2133 | 4462.097 | 0.88022 | 0.74782 | 38.9086
| 84 | 64.6571 | 116.3531 | -117.0617 | 7.2489 | 4358.3273 | 1.0269 | 0.85217 | 44.3377
| 82 | 63.1176 | 132.9749 | -133.7848 | 8.2845 | 4254.5576 | 1.1736 | 0.95072 | 49.4652
| 80 | 61.5782 | 149.5968 | -150.5079 | 9.32 | 4150.7879 | 1.3203 | 1.0435 | 54.2911
| 78 | 60.0387 | 166.2187 | -167.231 | 10.3556 | 4047.0182 | 1.467 | 1.1304 | 58.8154
| 76 | 58.4993 | 182.8405 | -183.9541 | 11.3911 | 3943.2485 | 1.6137 | 1.2116 | 63.038
| 74 | 56.9598 | 199.4624 | -200.6771 | 12.4267 | 3839.4788 | 1.7604 | 1.2869 | 66.959
| 72 | 55.4204 | 216.0843 | -217.4002 | 13.4623 | 3735.7091 | 1.9072 | 1.3565 | 70.5784
| 70 | 53.8809 | 232.7061 | -234.1233 | 14.4978 | 3631.9394 | 2.0539 | 1.4203 | 73.8962
| 68 | 52.3415 | 249.328 | -250.8464 | 15.5334 | 3528.1697 | 2.2006 | 1.4783 | 76.9124
| 66 | 50.802 | 265.9499 | -267.5695 | 16.5689 | 3424.4 | 2.3473 | 1.5304 | 79.627
| 64 | 49.2625 | 282.5717 | -284.2926 | 17.6045 | 3320.6303 | 2.494 | 1.5768 | 82.0399
| 62 | 47.7231 | 299.1936 | -301.0157 | 18.64 | 3216.8606 | 2.6407 | 1.6174 | 84.1512
| 60 | 46.1836 | 315.8155 | -317.7388 | 19.6756 | 3113.0909 | 2.7874 | 1.6522 | 85.9609
| 59 | 45.4139 | 324.1264 | -326.1004 | 20.1934 | 3061.2061 | 2.8607 | 1.6674 | 86.7527
| 58 | 44.6442 | 332.4373 | -334.4619 | 20.7112 | 3009.3212 | 2.9341 | 1.6812 | 87.469
| 57 | 43.8745 | 340.7483 | -342.8235 | 21.2289 | 2957.4364 | 3.0074 | 1.6935 | 88.11
| 56 | 43.1047 | 349.0592 | -351.185 | 21.7467 | 2905.5515 | 3.0808 | 1.7043 | 88.6755
| 55 | 42.335 | 357.3701 | -359.5466 | 22.2645 | 2853.6667 | 3.1541 | 1.7138 | 89.1656
| 54 | 41.5653 | 365.6811 | -367.9081 | 22.7823 | 2801.7818 | 3.2275 | 1.7217 | 89.5803
| 53 | 40.7955 | 373.992 | -376.2697 | 23.3001 | 2749.897 | 3.3008 | 1.7283 | 89.9197
| 52 | 40.0258 | 382.3029 | -384.6312 | 23.8178 | 2698.0121 | 3.3742 | 1.7333 | 90.1836
| 51 | 39.2561 | 390.6139 | -392.9927 | 24.3356 | 2646.1273 | 3.4475 | 1.7369 | 90.3721
| 50 | 38.4864 | 398.9248 | -401.3543 | 24.8534 | 2594.2424 | 3.5209 | 1.7391 | 90.4852
| 49 | 37.7166 | 407.2357 | -409.7158 | 25.3712 | 2542.3576 | 3.5942 | 1.7398 | 90.5229
| 48 | 36.9469 | 415.5467 | -418.0774 | 25.8889 | 2490.4727 | 3.6676 | 1.7391 | 90.4852
| 47 | 36.1772 | 423.8576 | -426.4389 | 26.4067 | 2438.5879 | 3.741 | 1.7369 | 90.3721
| 46 | 35.4075 | 432.1685 | -434.8005 | 26.9245 | 2386.703 | 3.8143 | 1.7333 | 90.1836
| 45 | 34.6377 | 440.4795 | -443.162 | 27.4423 | 2334.8182 | 3.8877 | 1.7283 | 89.9197
| 44 | 33.868 | 448.7904 | -451.5236 | 27.9601 | 2282.9333 | 3.961 | 1.7217 | 89.5803
| 43 | 33.0983 | 457.1013 | -459.8851 | 28.4778 | 2231.0485 | 4.0344 | 1.7138 | 89.1656
| 42 | 32.3285 | 465.4123 | -468.2467 | 28.9956 | 2179.1636 | 4.1077 | 1.7043 | 88.6755
| 41 | 31.5588 | 473.7232 | -476.6082 | 29.5134 | 2127.2788 | 4.1811 | 1.6935 | 88.11
| 40 | 30.7891 | 482.0341 | -484.9698 | 30.0312 | 2075.3939 | 4.2544 | 1.6812 | 87.469
| 35 | 26.9405 | 523.5888 | -526.7775 | 32.6201 | 1815.9697 | 4.6212 | 1.5978 | 83.1333
| 30 | 23.0918 | 565.1435 | -568.5853 | 35.209 | 1556.5455 | 4.9879 | 1.4783 | 76.9124
| 25 | 19.2432 | 606.6981 | -610.393 | 37.7979 | 1297.1212 | 5.3547 | 1.3225 | 68.8064
| 20 | 15.3945 | 648.2528 | -652.2007 | 40.3868 | 1037.697 | 5.7215 | 1.1304 | 58.8154
| 15 | 11.5459 | 689.8075 | -694.0085 | 42.9757 | 778.2727 | 6.0882 | 0.90217 | 46.9392
| 10 | 7.6973 | 731.3621 | -735.8162 | 45.5645 | 518.8485 | 6.455 | 0.63768 | 33.1779
| 5 | 3.8486 | 772.9168 | -777.6239 | 48.1534 | 259.4242 | 6.8217 | 0.33695 | 17.5315
| 0 | 0 | 814.4715 | -819.4317 | 50.7423 | 0 | 7.1885 | 0 | 0